Specification

.Isolation 3000VDC

.Industrial specification

.Fully compatible with serial RS422/485

.DC power supply (10~30V) Built in Surge Protector

.Auto Toggling by hardware

.Communication status can be monitored through LEDs

.Dip switch for selecting RS422/485 modes, Terminal Resistance

.Max. 10 Device Connectivity for RS422 Multi-Drop Mode

.Max. 32 Device Connectivity for RS485 Mode

Repeater RS422/485 signals to RS422/485. It is an efficient solution for applying advantages of RS422/485 to legacy RS422/485 devices. The repeater operates with no extra software installation. With simple DIP switch toggling, RS422 or RS485 can be selected. Also, the product is fully compatible with serial COM port in PC.

Using 4-wire RS485

4-Wire RS485 Networking is same as RS422 Multi-Drop Networking. RS422 device is used as master and RS485 device is used as slave in 4-Wire RS485 bus. Although RS422 and RS485 have different electrical standards, most manufacturers make ICs that uses both RS422 and RS485 interface. Therefore, RS422 Multi-Drop and 4-Wire RS485 can be considered equal.

However, there can be difference in software that controls them. Since our device can operate regardless of the application software, it is ok to use without any trouble. In this case, set RS422 Multi-Drop mode.

Applications

.RS-422/485 communication

.Utility meters

.Industrial process control

.Building automation

.Industrial-controlled Local Area Network

.Industrial PCs and PC peripherals devices

Serial Converter

| Mode | Asynchronous serial communication |
| --- | --- |
| Speed | Up to 460.8kbps |
| Connector | RS422/485 : Terminal Block 5P 5.08 ,RS422/485 : Terminal Block 7P 5.08mm |
| Signals | TX+,TX-,RX+,RX- for RS422/485 |
| Protection | 15KV ESD Protection for all signals RS422/485 signals Surge Protection |
| Distance | Max 1.2Km 115.2Kbps,24AWG twisted pair cable |
| Data Bits | 5,6,7,8 |
| Stop Bits | 1,1.5,2 |
| Parity | None,Even,Odd,Space,Mark |
| RS422 mode | Point to Point,Multi Drop |
| Switch | RS422 Term.Resistor setting |
|  | RS485 Term.Resistor setting |
|  | RS422/485 selection |

Software

| OS | No Software Required |
| --- | --- |

Hardware

| Power Input | 10~30VDC Terminal Block 7P 5.08mm |
| --- | --- |
| Power Consumption | 53mA@24VDC |
| LED | Power,TXD,RXD |
| Isolation | Optical 3000 VDC max |
| Dimensions | 42.5(W)x22.5(H)106(D)mm |
| Weight | 86g |
| Terminal Block | 12~24AWG |

Terminal Block 7 PIN Define

|  | RS422 | RS422Multi-Drop/RS485 4W | RS485 |
| --- | --- | --- | --- |
| 1 | TX+ | TX+ |  |
| 2 | TX- | TX+ |  |
| 3 | RX+ | RX+ | DATA+ |
| 4 | RX- | RX- | DATA- |
| 5 | SG | SG | SG |
| 6 | VCC | VCC | VCC |
| 7 | GND | GND | GND |

Terminal Block 5 PIN Define

|  | RS422 | RS422Multi-Drop/RS485 4W | RS485 |
| --- | --- | --- | --- |
| 1 | SG | SG | SG |
| 2 | RX-- | RX- | DATA- |
| 3 | RX+ | RX+ | DATA+ |
| 4 | TX- | TX- |  |
| 5 | TX+ | TX+ |  |

DIP SW1

| DIP SW SET | 1 | 2 | 3 | 4 |  |
| --- | --- | --- | --- | --- | --- |
| 0=OFF,1=ON | 0 | 0 | 0 | x | RS422 |
|  | 0 | 0 | 1 | x | RS422 |
|  | 1 | 0 | 1 | x | RS485 4W,RS422 Multi Drop |
|  | 0 | 1 | 0 | x | RS485 2W |
|  | x | x | x | 1 | RS422/485 Term.Resistor ON |

DIP SW2 All SW Only RS422/485 Term.Resistor ON

Environmental

| Operating Temp | -30~75℃ |
| --- | --- |
| Storage Temp | -40~85℃ |
| Humidity | 5~95% Non-Condensing |
| Case | PC |

Approvals

CE ,FCC RoHs Compliant

Dimension